## Rule 101B (5)(b)
NGR Part 10, Rule 101B 5(b) - Service and Access Information: Matters Expected to Affect Capacity (Last Reviewed 08/04/2026)
This table contain matters (projects or matinenance activities) that have the potential to affect the capacity of JGN's Large Distribution Mains (Defined as a pipeline which has a flowrate equal to or greater than 10TJ/day and a maximum operating pressure equal to or above 4 MPa as defined by the AEMC Energy Rules Website). For completion, other significant projects that do not affect capacity may also be included.
Status | Indentifier | Date From | Date to | Project Name | Asset Effected | Matters Effecting Capacity | Expected impact on capacity during the period (TJ) | Commentary | Last Updated
Open or Closed | YY-### | Date DD/MM/YY | Date DD/MM/YY | Project Name | List one or more assets | What is causing the change to capacity or where no change to capacity | TJ (if known) | Further explanation | Date DD/MM/YY
Closed | 25-001 | 2025-04-26 | -- | JGN Trunk pressure increase project | Wilton PLS to Wollongong PRS facilities and Wilton PLS to Kooragang Island TRS facilities | New operating pressure. The operating pipeline pressure will be required to be increased to meet the demand at Kurri Kurri Offtake Meter Station (KKOMS) On going increase. | 16 | Increase in capacity expected due to the pressure increase project. | 2025-05-05
Closed | 25-002 | 2025-10-20 | 2025-11-30 | Northern Trunk Validation Digs | Licence 7 | No pressure redution is planned, however may be required. | N/A | During works no pressure reduction was required. | 2025-12-02
Open | 26-001 | 2026-01-05 | 2026-04-24 | MSP S8 S9 Pressure Reduction | JGN Trunk | JGN max set point is 4.8MPa but operating pressure is based upon APA pressure. APA will reduce Wilton inlet pressure to 4.2MPa (for normal maintenance) or 3.8MPa (in case of rectification work) for the purpose of integrity digs (identifying defects) along MSP. | CLP from 4.8MPa to 4.2MPa = ~19 TJ CLP from 4.2MPa to 3.8MPa = ~13 TJ CLP from 4.8MPa to 3.8MPa = ~32 TJ | Currently ongoing works. Not within our control. Modelling still being completed. Notice to market may be required. Planned reinstatement of ROP is 10th of Apri, 2026. Will change planned date once it has occurred. | 2026-04-08
Open | 26-002 | TBC | TBC | Validation Digs (Still TBC) | Licence 1 & CPM | No pressure redution is planned, however may be required. | N/A | Dates still to be confirmed. | 2026-04-08
Closed | 26-003 | 2026-02-04 | 2026-02-11 | MSP S8 S9 Pressure Reduction | JGN Trunk | JGN max set point is 4.8MPa but operating pressure is based upon APA pressure. APA will reduce Wilton inlet pressure to 3.8MPa in order to perform integrity digs and rectification works along the MSP. | CLP from 4.2MPa to 3.8MPa = ~13 TJ CLP from 4.8MPa to 3.8MPa = ~32 TJ | Temporary rectification works have been completed. Not within our control. Modelling still being completed. Notice to market may be required. | 2026-03-13
Open | 26-004 | TBC | TBC | Validation Digs (Still TBC) | Licence 7 & 8 | No pressure redution is planned, however may be required. | N/A | Dates still to be confirmed. | 2026-04-08